## General parameters
year_start | 1998 | reference start year used in the simulation
year_end | 2014 | reference end year used in the simulation
column_start | 1 | index of column (first column = 1) corresponding to year_start in time series Excel sheets (this needs to be the same across all Excel sheets)
rho | 1000 | density of water (kg/m^3) (introduced in eq. S3)
g | 9.81 | gravitational acceleration (m/s^2) (introduced in eq. S8)
T_fill_thres | 1 | represents number of years of filling as threshold for determining f_reg if left unspecified by user (see sheet "Hydropower plant parameters"). Default/recommended is unity, so f_reg represents the fraction of annual mean inflow that would take exactly one year to fill reservoir.
LOEE_allowed | 0 | allowed Loss of Energy Expectation as percentage of yearly ELCC
option_storage | 0 | wish to activate pumped storage module (Note 7) for at least one hydropower plant or not? (0 = no, 1 = yes)

## Hydropower plant parameters
HPP_name | name of hydropower plant in simulation | Bui | Buyo
HPP_active | used to include (= 1) or exclude (= 0) plant from current run | 1 | 1
HPP_name_data_inflow | name of corresponding worksheet in the "data" Excel sheets from which to pull data on reservoir inflow (hourly inflow in m^3/s; hours in rows, years in columns) | Bui | Buyo
HPP_name_data_outflow_prescribed | name of corresponding worksheet in the "data" Excel sheets from which to pull data on prescribed (environmental/irrigation) outflow (hourly in m^3/s; hours in rows, years in columns) | Bui | Buyo
HPP_name_data_CF_solar | name of corresponding worksheet in the "data" Excel sheets from which to pull data (hourly solar CF as fraction/percentage; hours in rows, years in columns) | Bui | Buyo
HPP_name_data_CF_wind | name of corresponding worksheet in the "data" Excel sheets from which to pull data (hourly wind CF as fraction/percentage; hours in rows, years in columns) | Bui | Buyo
HPP_name_data_evaporation | name of corresponding worksheet in the "data" Excel sheets from which to pull data (evaporation flux in kg/m^2/s; hours in rows, years in columns) | Bui | Buyo
HPP_name_data_precipitation | name of corresponding worksheet in the "data" Excel sheets from which to pull data (precipitation flux in kg/m^2/s; hours in rows, years in columns) | Bui | Buyo
HPP_name_data_load | name of corresponding worksheet in the "data" Excel sheets from which to pull data (hourly load normalised to a mean of unity) | Bui | Buyo
HPP_name_data_bathymetry | name of corresponding worksheet in the "data" Excel sheets from which to pull data (first column: volume in m^3; second: surface area in m^2; third: head in m) | Bui | Buyo
c_solar_relative | fraction of solar in the solar/wind portfolio | 1 | 1
h_max | maximum head in m | 80 | 36.1
A_max | maximum lake area in m^2 | 440000000 | 900000000
V_max | maximum lake volume in m^3 | 12570000000 | 8300000000
V_initial_frac | initial filling fraction of lake volume | 0.8 | 0.8
P_r_turb | installed capacity in MW | 400 | 165
Q_max_turb | maximum discharge (total of all turbines) in m^3/s | 637.105 | 582.3951
no_turbines | number of turbines (units) | 3 | 3
eta_turb | turbine efficiency as fraction | 0.8 | 0.8
dP_ramp_turb | turbine ramp rate in % of full capacity / min | 0.0256 | 0.0256
f_stop | fraction of lake volume at which production stops | 0.1 | 0.1
f_restart | fraction of lake volume at which production restarts after stopping | 0.2 | 0.2
f_opt | optimal filling fraction f_opt (eq. S4, S5) | 0.8 | 0.8
f_spill | fraction f_spill beyond which spilling starts (eq. S7) | 0.95 | 0.95
f_reg | [leave empty if unsure - default determined by storage size will be used] which fraction of the incoming water is allocated for regulated use
min_load_turbine | minimum load on one single turbine to ensure high-efficiency range (fraction) | 0.35 | 0.35
d_min | [leave empty if unsure - default determined by minimum turbine load will be used] which fraction of the regulated use (two lines above) must be dispatched at stable level (eq. S4, S5)
alpha | alpha (eq. S6) for conventional HPP operation rule curve (eq. S4) | 0.66667 | 0.66667
gamma_hydro | gamma (eq. S4) for conventional HPP operation rule curve (eq. S4) | 10 | 10
mu | mu parameter to control spilling (eq. S7) | 0.1 | 0.1
f_size | this percentile controls the amount of allowed VRE overproduction (represents the % of time in which hydro+VRE may not exceed average ELCC) | 90 | 90
p_exceedance | this percentile is used to calculate the exceedance probability of delivered power (guaranteed capacity, MW). For P90, use 90; for P95, use 95, etc. | 90 | 90
V_lower_max | [leave empty if not using pumped storage assessment] lower lake volume in m^3 | 12570000
V_lower_initial_frac | [leave empty if not using pumped storage assessment] initial filling fraction of lower lake volume | 0.8
P_r_pump | [leave empty if not using pumped storage assessment] pump capacity in MW | 100
Q_max_pump | [leave empty if not using pumped storage assessment] pump maximum discharge in m^3/s | 101.9368
eta_pump | [leave empty if not using pumped storage assessment] pump efficiency as fraction | 0.8
dP_ramp_pump | [leave empty if not using pumped storage assessment] pump ramp rate in % of full capacity / min | 0.0256

## Simulation accuracy
N_ELCC | 1000 | This number defines the amount of discrete steps between 0 and max(E_hydro + E_solar + E_wind)
psi_min_threshold | 0 | When min(Psi) (eq. S21) is lower than this threshold, no further refinement loops are performed
f_init_BAL_start | 0 | These values are used to get a good initial guess for the range of the ELCC for BAL. This is the lower value in the guessed range
f_init_BAL_step | 0.2 | These values are used to get a good initial guess for the range of the ELCC for BAL. This is the step size in the guessed range
f_init_BAL_end | 2 | These values are used to get a good initial guess for the range of the ELCC for BAL. This is the upper value in the guessed range
N_refine_BAL | 2 | Number of refinement loops for equilibrium search for min(Psi) in BAL (see eq. S21)
X_max_BAL | 2 | Number of loops for iterative estimation of P_stable,BAL (see eq. S9 & explanation below eq. S19)
f_init_STOR_start | 0 | These values are used to get a good initial guess for the range of the ELCC for STOR. This is the lower value in the guessed range
f_init_STOR_step | 0.2 | These values are used to get a good initial guess for the range of the ELCC for STOR. This is the step size in the guessed range
f_init_STOR_end | 2 | These values are used to get a good initial guess for the range of the ELCC for STOR. This is the upper value in the guessed range
N_refine_STOR | 2 | Number of refinement loops for equilibrium search for min(Psi) in STOR (see eq. S21)
X_max_STOR | 2 | Number of loops for iterative estimation of P_stable,STOR (see eq. S9 & explanation below eq. S19)